## Line_data_20150915
These data are giving the situation on the internal equipment as of 20150915.
According to the commisioning dates foreseen in the Federal Development Plan, no change in data is to be foreseen before 20151101.
Substation 1 | Substation 1 - Full name | Substation 2 | Substation 2 - Full name | U | U/Nr. | Length | Pnom | R | X | ωC/2
[5 empty] | (kV) | (Km) | (MVA) | (Ω) | (Ω) | (μS)
ACHEN | ACHENE | GRAMM | GRAMME | 380 | 380 / 10 | 36.9 | 1316.3 | 1.144 | 12.103 | 70.737
AUBAN | AUBANGE | BRUME | BRUME | 380 | 380 / 13 | 104.4 | 1439 | 2.95 | 31.27 | 200.38
AVLGM | AVELGEM | IZGEM | IZEGEM | 380 | 380 / 47 | 22.8 | 1439 | 0.706 | 7.475 | 43.825
AVLGM | AVELGEM | IZGEM | IZEGEM | 380 | 380 / 46 | 22.8 | 1439 | 0.706 | 7.475 | 43.825
AVLGM | AVELGEM | HORTA | HORTA | 380 | 380 / 101 | 39.7 | 1316 | 1.23 | 13.02 | 73.445
AVLGM | AVELGEM | HORTA | HORTA | 380 | 380 / 102 | 39.7 | 1439 | 1.248 | 13 | 76.478
BRUEG | BRUEGEL | BUGG+ | BUGGENHOUT | 380 | 380 / 35 | 15.9 | 1316 | 0.61 | 5.11 | 29.9
BRUEG | BRUEGEL | BUGG+ | BUGGENHOUT | 380 | 380 / 36 | 15.9 | 1439 | 0.5 | 5.25 | 30.9
BRUEG | BRUEGEL | COURC | COURCELLES | 380 | 380 / 34 | 47.3 | 1439 | 1.466 | 15.514 | 91.3
BRUEG | BRUEGEL | MEKI+ | MEKINGEN | 380 | 380 / 33 | 14 | 1316 | 0.451 | 4.625 | 27.09
BRUME | BRUME | COO | COO | 380 | 380 / 4 | 2 | 1316 | 0.062 | 0.656 | 3.86
BRUME | BRUME | COO | COO | 380 | 380 / 3 | 2 | 1316 | 0.062 | 0.656 | 3.86
BRUME | BRUME | GRAMM | GRAMME | 380 | 380 / 1 | 44.3 | 1316 | 1.373 | 14.53 | 82
BRUME | BRUME | GRAMM | GRAMME | 380 | 380 / 2 | 44.3 | 1526 | 1.373 | 14.53 | 85.19
BUGG+ | BUGGENHOUT | MERCA | MERCATOR | 380 | 380 / 36 | 15.5 | 1439 | 0.48 | 5.084 | 29.4
BUGG+ | BUGGENHOUT | MERCA | MERCATOR | 380 | 380 / 35 | 15.5 | 1316 | 0.59 | 5 | 29.3
BUGG+ | BUGGENHOUT | VERBR | VERBRANDE BRUG | 380 | 380 / 36 | 21.7 | 1439 | 0.673 | 7.118 | 41.729
BUGG+ | BUGGENHOUT | VERBR | VERBRANDE BRUG | 380 | 380 / 35 | 21.7 | 1526 | 0.658 | 6.91 | 41.729
CHAMP | CHAMPION (NAMUR) | COURC | COURCELLES | 380 | 380 / 56 | 44.1 | 1439 | 1.367 | 14.465 | 85.122
CHAMP | CHAMPION (NAMUR) | GRAMM | GRAMME | 380 | 380 / 32 | 32.2 | 1439 | 0.999 | 10.562 | 62.123
COURC | COURCELLES | GOUY | GOUY | 380 | 380 / 58 | 1.8 | 1439 | 0.06 | 0.59 | 3.5
COURC | COURCELLES | GOUY | GOUY | 380 | 380 / 57 | 1.7 | 1316 | 0.05 | 0.56 | 3.3
COURC | COURCELLES | MEKI+ | MEKINGEN | 380 | 380 / 33 | 33.4 | 1316 | 1.03 | 10.95 | 64.1
COURC | COURCELLES | STAM+ | ST-AMAND | 380 | 380 / 31 | 12.6 | 1316 | 0.39 | 4.132 | 24.318
DOEL | DOEL | MERCA | MERCATOR | 380 | 380 / 52 | 22.8 | 1316 | 0.707 | 7.478 | 44
DOEL | DOEL | MERCA | MERCATOR | 380 | 380 / 54 | 22.2 | 1439 | 0.799 | 6.838 | 40
DOEL | DOEL | MERCA | MERCATOR | 380 | 380 / 51 | 22.8 | 1316 | 0.707 | 7.478 | 44
DOEL | DOEL | ZANDV | ZANDVLIET | 380 | 380 / 25 | 6.8 | 1316 | 0.243 | 2.399 | 12.001
DOEL | DOEL | HORTA | HORTA | 380 | 380 / 73 | 70.6 | 1316 | 2.26 | 22.59 | 132.725
DROGE | DROGENBOS | MEKI+ | MEKINGEN | 380 | 380 / 33 | 10.3 | 1439 | 0.319 | 3.38 | 19.807
EEKLN | EEKLO NOORD | HORTA | HORTA | 380 | 380 / 103 | 12 | 1439 | 0.372 | 3.936 | 23.2
GRAMM | GRAMME | HERD+ | HERDEREN | 380 | 380 / 11 | 43.3 | 1316 | 1.26 | 13.99 | 80.1
GRAMM | GRAMME | RIMIE | RIMIERE | 380 | 380 / 7 | 14.6 | 1316 | 0.453 | 4.789 | 27
GRAMM | GRAMME | STAM+ | ST-AMAND | 380 | 380 / 31 | 56.4 | 1316 | 1.747 | 18.499 | 108.9
GRAMM | GRAMME | TIHA1 | TIHANGE 1 | 380 | 380 / 5 | 2.9 | 1316 | 0.089 | 0.951 | 5.597
GRAMM | GRAMME | TIHA1 | TIHANGE 1 | 380 | 380 / 6 | 2.9 | 1316 | 0.089 | 0.951 | 5.597
GRAMM | GRAMME | TIHA2 | TIHANGE 2 | 380 | 380 / 17 | 2.6 | 1439 | 0.081 | 0.853 | 5.02
GRAMM | GRAMME | TIHA3 | TIHANGE 3 | 380 | 380 / 18 | 3.3 | 1439 | 0.102 | 1.082 | 6.37
HERD+ | HERDEREN | LIXHE | LIXHE | 380 | 380 / 11 | 10.1 | 1439 | 0.32 | 3.35 | 18.9
HERD+ | HERDEREN | VANYK | VAN EYCK | 380 | 380 / 11 | 43 | 1316 | 1.245 | 13.877 | 75.535
HORTA | HORTA | RODE+ | RODENHUIZE | 380 | 380 / 74 | 14.2 | 1439 | 0.446 | 4.646 | 27.355
LINT | LINT | MASSE | MASSENHOVEN | 380 | 380 / 61 | 14.06 | 1441 | 0.46 | 4.56 | 25.084
LINT | LINT | MERCA | MERCATOR | 380 | 380 / 61 | 21.1 | 1439 | 0.654 | 6.92 | 36.9
LINT | LINT | MERCA | MERCATOR | 380 | 380 / 59 | 21.1 | 1439 | 0.654 | 6.92 | 36.9
MASSE | MASSENHOVEN | MEERH | MEERHOUT | 380 | 380 / 21 | 32.5 | 1439 | 1.008 | 10.66 | 62.7
MASSE | MASSENHOVEN | MERCA | MERCATOR | 380 | 380 / 60 | 35 | 1439 | 1.091 | 11.545 | 61.6
MEERH | MEERHOUT | VANYK | VAN EYCK | 380 | 380 / 23 | 57.5 | 1439 | 1.782 | 18.86 | 110.431
MERCA | MERCATOR | RODE+ | RODENHUIZE | 380 | 380 / 74 | 34.2 | 1316 | 1.075 | 11.213 | 66.1
STAM+ | ST-AMAND | TERGN | TERGNEE | 380 | 380 / 31 | 7.5 | 1439 | 0.232 | 2.46 | 13.88
AUBAN | AUBANGE | HEINS | HEINSCH | 220 | 220 / 507 | 15 | 405 | 1.603 | 4.41 | 24.49
AUBAN | AUBANGE | LATO+ | LATOUR | 220 | 220 / 515 | 15.5 | 339 | 1.194 | 6.169 | 21.7
AUBAN | AUBANGE | SMARD | ST-MARD | 220 | 220 / 516 | 21.1 | 339 | 1.62 | 8.398 | 29.5
AUBAN | AUBANGE | VILLE | VILLEROUX | 220 | 220 / 506 | 47.2 | 405 | 4.012 | 14.16 | 77.078
AWIRS | AWIRS | LEVAL | LE VAL | 220 | 220 / 521 | 6.6 | 416 | 0.33 | 2.64 | 9.325
AWIRS | AWIRS | RIMIE | RIMIERE | 220 | 220 / 535 | 7.4 | 372 | 0.472 | 3.129 | 10.03
BERNE | BERNEAU | JUPIL | JUPILLE | 220 | 220 / 531 | 17.8 | 678 | 0.627 | 3.293 | 147.967
BERNE | BERNEAU | LIXHE | LIXHE | 220 | 220 / 541 | 6.5 | 534 | 0.184 | 1.005 | 115.767
BRUME | BRUME | HOUF+ | HOUFFALIZE | 220 | 220 / 504 | 27.5 | 474 | 1.623 | 8.14 | 48.12
HEINS | HEINSCH | VILLE | VILLEROUX | 220 | 220 / 505 | 33.2 | 405 | 3.433 | 9.67 | 54.21
HOUF+ | HOUFFALIZE | VILLE | VILLEROUX | 220 | 220 / 504 | 25.5 | 474 | 1.51 | 7.53 | 44.8
JUPIL | JUPILLE | RIMIE | RIMIERE | 220 | 220 / 538 | 21.3 | 416 | 1.15 | 8.92 | 30.4
JUPIL | JUPILLE | ROMSE | ROMSEE | 220 | 220 / 534 | 5 | 300 | 0.45 | 2.17 | 6.5
LATO+ | LATOUR | SMARD | ST-MARD | 220 | 220 / 515 | 5.6 | 339 | 0.431 | 2.223 | 7.84
LEVAL | LE VAL | RIMIE | RIMIERE | 220 | 220 / 522 | 13.4 | 372 | 0.767 | 5.29 | 18.701
MARC+ | MARCOURT | RIMIE | RIMIERE | 220 | 220 / 501 | 38 | 405 | 3.23 | 11.3 | 62.054
MARC+ | MARCOURT | SENO+ | #N/A | 220 | 220 / 501 | 26.8 | 405 | 2.278 | 8.04 | 43.76
RIMIE | RIMIERE | SERAI | SERAING | 220 | 220 / 533 | 11.4 | 395 | 0.66 | 4.63 | 15.9
ROMSE | ROMSEE | SERAI | SERAING | 220 | 220 / 530 | 14.3 | 395 | 0.83 | 5.81 | 20.1
SENO+ | #N/A | VILLE | VILLEROUX | 220 | 220 / 501 | 2.6 | 405 | 0.6266 | 2.145 | 4.2458

## Interconnections_data_20150915
These data are coming from the ENTSO-e reference case, situation as of 20150915. X-node is in the electrical middle of the line.
These data will be updated when ENTSO-e reference case is updated.
Substation 1 | Substation 1 - Full name | X-node | Substation 2 - Full name | U | U/Nr. | Length | Pnom | R | X | ωC/2
[5 empty] | (kV) | (Km) | (MVA) | (Ω) | (Ω) | (μS)
MONCE | MONCEAU | XMO_CH21 | CHOOZ | 220 | 220 / 48 | 29.4 | 403 | 1.6625 | 11.7168 | 76.4786
AUBAN | AUBANGE | XAU_SA21 | SANEM | 220 | 220 / 512 | 5.75 | 400 | 0.3335 | 2.3314 | 16.1848
AUBAN | AUBANGE | XAU_MO22 | MOULAINE | 220 | 220 / 513 | 7.85 | 442 | 0.44033 | 3.4752 | 13.7145
AUBAN | AUBANGE | XAU_M.21 | MOULAINE | 220 | 220 / 514 | 1.935 | 442 | 0.10687 | 0.80656 | 6.2631
ACHEN | ACHENE | XAC_LO11 | LONNY | 380 | 380 / 19 | 31.5 | 1316 | 0.7846 | 9.5414 | 94.1168
VANYK | VAN EYCK | XVY_MB12 | MAASBRACHT | 380 | 380 / 27 | 5.5 | 1420 | 0.13657 | 1.576 | 22.837
VANYK | VAN EYCK | XVY_MB11 | MAASBRACHT | 380 | 380 / 28 | 5.5 | 1350 | 0.13836 | 1.5778 | 22.9572
ZANDV | ZANDVLIET | XZA_BS11 | BORSSELE | 380 | 380 / 29 | 23.7 | 1645 | 0.57908 | 6.5262 | 98.4138
ZANDV | ZANDVLIET | XZA_GT11 | GEERTRUIDENBERG | 380 | 380 / 30 | 33.55 | 1645 | 0.81868 | 9.2268 | 139.0776
AVLGM | AVELGEM | XAV_MA11 | MASTAING | 380 | 380 / 79 | 38.45 | 1316 | 0.94547 | 11.482 | 95.5338
AVLGM | AVELGEM | XAV_AV11 | AVELIN | 380 | 380 / 80 | 21.65 | 1528 | 0.86301 | 8.8153 | 78.4364

## Transformer_data_20150915
These data are giving the situation on the internal equipment as of 20150915.
According to the commisioning dates foreseen in the Federal Development Plan, no change in data is to be foreseen before 20151101.
PUTM | Substation | Substation - Full name | U / Expl.Nr | V1 | V2 | V3 | Pnom1 | Pnom2 | Pnom3 | Zcc12 | Zcc13 | Zcc23 | Min Tap | Nom Tap | Max Tap | ∆V /tap | ∆V /tap
|  |  |  | (kV) | (kV) | (kV) | (MVA) | (MVA) | (MVA) | (%) | (%) | (%) | # | # | # | (kV) | (%Unom)
ACHEN380T 1 380/ 70/36 T3 | ACHEN | ACHENE | 380 / T 1 | 380 | 70 | 36 | 220 | 220 | 50 | 20.7 | 12.1 | 6.89 | 1 | 18 | 35 | -3.5294 | -0.88235
AUBAN220T 9 220/ 70/15 T3 | AUBAN | AUBANGE | 220 / T 9 | 220 | 70 | 15 | 90 | 90 | 30 | 12.77 | 13.33 | 7.05 | 23 | 12 | 1 | 3.6445 | 1.6417
AUBAN380T 1 380/220/36 T3 | AUBAN | AUBANGE | 380 / T 1 | 380 | 220 | 36 | 300 | 300 | 15 | 15.42 | 6.97 | 5.45 | 1 | 11 | 24 | 1.84 | 0.74974
AUBAN380T 2 380/220/36 T3 | AUBAN | AUBANGE | 380 / T 2 | 380 | 220 | 36 | 300 | 300 | 15 | 15.1 | 6.1 | 4.58 | 1 | 11 | 24 | 1.8338 | 0.74711
AVLGM380T 1 380/150/36 T3 | AVLGM | AVELGEM | 380 / T 1 | 380 | 150 | 36 | 450 | 450 | 15 | 17.87 | 2.17 | 1.23 | 1 | 12 | 24 | 1.5117 | 0.91572
AVLGM380T 2 380/150/36 T3 | AVLGM | AVELGEM | 380 / T 2 | 380 | 150 | 36 | 555 | 555 | 15 | 22.4 | 1.98 | 1.13 | 1 | 12 | 24 | 1.5217 | 0.92452
AWIRS220T 7 220/150/15 T3 | AWIRS | AWIRS | 220 / T 7 | 220 | 150 | 15 | 375 | 375 | 25 | 14.1 | 8.95 | 6.95 | 1 | 7 | 21 | 1.0264 | 0.70837
AWIRS220T 8 220/ 70/70 T3 | AWIRS | AWIRS | 220 / T 8 | 220 | 70 | 70 | 160 | 80 | 80 | 14.87 | 14.79 | 27.59 | 1 | 7 | 19 | -2.8083 | -1.2481
BRUEG380T 1 380/150/36 T3 | BRUEG | BRUEGEL | 380 / T 1 | 380 | 150 | 36 | 450 | 450 | 15 | 19.4 | 2.1 | 1.21 | 1 | 12 | 20 | 1.5625 | 0.94933
BRUEG380T 2 380/150/36 T3 | BRUEG | BRUEGEL | 380 / T 2 | 380 | 150 | 36 | 450 | 450 | 150 | 17.9 | 21.6 | 12.5 | 1 | 12 | 24 | 1.6025 | 1.0111
BRUME220T 3 220/ 70 T2 | BRUME | BRUME | 220 / T 3 | 220 | 70 |  | 90 |  |  | 15.2 |  |  | 1 | 10 | 17 | -3.0543 | -1.3575
BRUME380T 1 380/220/36 T3 | BRUME | BRUME | 380 / T 1 | 380 | 220 | 36 | 300 | 300 | 15 | 15.4 | 6.95 | 5.46 | 1 | 11 | 24 | 1.84 | 0.74974
BRUME380T 4 380/ 70/36 T3 | BRUME | BRUME | 380 / T 4 | 380 | 70 | 36 | 110 | 110 | 2 | 20.8 | 2.04 | 1.61 | 1 | 17 | 33 | -3.75 | -0.9375
CHAMP380T11 380/ 70/36 T3 | CHAMP | CHAMPION (NAMUR) | 380 / T11 | 380 | 70 | 36 | 220 | 220 | 50 | 20.9 | 12.1 | 6.9 | 1 | 18 | 35 | -3.5294 | -0.88235
CHAMP380T12 380/ 70/36 T3 | CHAMP | CHAMPION (NAMUR) | 380 / T12 | 380 | 70 | 36 | 220 | 220 | 2 | 22.52 | 0.5 | 0.27 | 1 | 17 | 33 | -3.75 | -0.9375
DROGE380T 4 380/150/36 T3 | DROGE | DROGENBOS | 380 / T 4 | 380 | 150 | 36 | 500.1 | 500.1 | 15 | 19.81 | 2.07 | 1.16 | 1 | 12 | 24 | -1.6692 | -1.0117
EEKLN380T 1 380/150/36 T3 | EEKLN | EEKLO NOORD | 380 / T 1 | 380 | 150 | 36 | 450 | 450 | 15 | 17.69 | 2.16 | 1.26 | 1 | 12 | 24 | 1.5225 | 0.92396
GOUY 380T 3 380/150/36 T3 | GOUY | GOUY | 380 / T 3 | 380 | 150 | 36 | 450 | 450 | 15 | 18.08 | 2.15 | 1.24 | 1 | 12 | 24 | 1.5142 | 0.9184
GOUY 380T 4 380/150/36 T3 | GOUY | GOUY | 380 / T 4 | 380 | 150 | 36 | 450 | 450 | 15 | 18.01 | 2.14 | 1.23 | 1 | 12 | 24 | 1.5225 | 0.92396
GRAMM380T 1 380/150/36 T3 | GRAMM | GRAMME | 380 / T 1 | 380 | 150 | 36 | 450 | 450 | 150 | 18.26 | 22.66 | 12.8 | 1 | 12 | 24 | 1.6025 | 1.0111
HEINS220T11 220/ 70/15 T3 | HEINS | HEINSCH | 220 / T11 | 220 | 70 | 15 | 90 | 90 | 30 | 11.54 | 12.16 | 7.72 | 1 | 7 | 19 | -3.75 | -1.6667
HOUFF220T11 220/ 70/15 T3 | HOUFF | HOUFFALIZE | 220 / T11 | 220 | 70 | 15 | 60 | 60 | 20 | 11.4 | 12.2 | 23.5 | 1 | 7 | 19 | -3.75 | -1.6667
IZGEM380T 1 380/150/36 T3 | IZGEM | IZEGEM | 380 / T 1 | 380 | 150 | 36 | 500.1 | 500.1 | 15 | 19.73 | 2.07 | 1.16 | 1 | 12 | 24 | 1.5358 | 0.93092
IZGEM380T 2 380/150/36 T3 | IZGEM | IZEGEM | 380 / T 2 | 380 | 150 | 36 | 450 | 450 | 15 | 17.57 | 2.16 | 1.27 | 1 | 12 | 24 | 1.5225 | 0.92396
JUPIL220T 5 220/ 70/70 T3 | JUPIL | JUPILLE | 220 / T 5 | 220 | 70 | 70 | 160 | 160 | 80 | 13.92 | 13.97 | 26.35 | 19 | 13 | 1 | 2.8125 | 1.25
JUPIL220T 7 220/150/15 T3 | JUPIL | JUPILLE | 220 / T 7 | 220 | 150 | 15 | 300 | 300 | 50 | 11.98 | 18.46 | 15.39 | 1 | 7 | 13 | 3.12 | 2
LINTT380T 1 380/150/36 T3 | LINT | LINT | 380 / T 1 | 380 | 150 | 36 | 450 | 450 | 15 | 17.99 | 2.13 | 1.23 | 1 | 12 | 24 | 1.5242 | 0.92497
LINTT380T 2 380/150/36 T3 | LINT | LINT | 380 / T 2 | 380 | 150 | 36 | 450 | 450 | 15 | 17.64 | 2.15 | 1.26 | 1 | 12 | 24 | 1.5225 | 0.92396
LIXHE220T 7 220/150/15 T3 | LIXHE | LIXHE | 220 / T 7 | 220 | 150 | 15 | 300 | 300 | 50 | 12 | 19.22 | 16.27 | 1 | 7 | 13 | 3.12 | 2
LIXHE380T 6 380/220/36 T3 | LIXHE | LIXHE | 380 / T 6 | 380 | 220 | 36 | 600 | 600 | 15 | 15.3 | 8.89 | 8.5 | 1 | 11 | 24 | 1.8377 | 0.74855
MARCO220T11 220/ 70/15 T3 | MARCO | MARCOURT | 220 / T11 | 220 | 70 | 15 | 85 | 85 | 20 | 11.31 | 8.87 | 7.72 | 1 | 12 | 26 | -2.3214 | -1.0552
MASSE380T 1 380/150/36 T3 | MASSE | MASSENHOVEN | 380 / T 1 | 380 | 150 | 36 | 450 | 450 | 15 | 18.12 | 2.13 | 1.23 | 1 | 12 | 24 | 1.5225 | 0.92396
MEERH380T 1 380/150/36 T3 | MEERH | MEERHOUT | 380 / T 1 | 380 | 150 | 36 | 472.5 | 472.5 | 157.5 | 18.2851 | 22.7 | 13 | 1 | 13 | 24 | 1.7435 | 1.1
MEERH380T 2 380/150/36 T3 | MEERH | MEERHOUT | 380 / T 2 | 380 | 150 | 36 | 500.1 | 500.1 | 15 | 19.8 | 2.06 | 1.16 | 1 | 12 | 24 | 1.5117 | 0.91572
MERCA380T 1 380/150/36 T3 | MERCA | MERCATOR | 380 / T 1 | 380 | 150 | 36 | 450 | 450 | 150 | 18.22 | 22.05 | 12.59 | 1 | 12 | 24 | 1.6025 | 1.0111
MERCA380T 2 380/150/36 T3 | MERCA | MERCATOR | 380 / T 2 | 380 | 150 | 36 | 555 | 555 | 15 | 22.93 | 2.09 | 1.34 | 1 | 12 | 24 | 1.505 | 0.91334
MONCE220T12 220/150/6 T3 | MONCE | MONCEAU | 220 / T12 | 220 | 150 | 6 | 290 | 290 | 20 | 10.4 | 24.48 | 22.09 | 1 | 10 | 19 | 2.0688 | 1.3344
RIMIE220T 3 220/ 70/70 T3 | RIMIE | RIMIERE | 220 / T 3 | 220 | 70 | 70 | 160 | 160 | 80 | 12.51 | 12.51 | 20.73 | 21 | 11 | 1 | 3.814 | 1.6951
RIMIE380T 8 380/220/36 T3 | RIMIE | RIMIERE | 380 / T 8 | 380 | 220 | 36 | 300 | 300 | 50 | 14.58 | 15.7 | 11 | 1 | 11 | 24 | 1.8338 | 0.74711
RIMIE380T 9 380/220/21 T2 | RIMIE | RIMIERE | 380 / T 9 | 380 | 220 | 21 | 300 | 300 | 65 | 12.74 | 13.76 | 9.6 | 1 | 1 | 1
RIMIE380T 9 380/220/36 T3 | RIMIE | RIMIERE | 380 / T 9 | 380 | 220 | 36 | 300 | 300 | 50 | 14.58 | 15.7 | 11 | 1 | 11 | 24 | 1.8338 | 0.74711
RODEN380T 1 380/150/36 T3 | RODEN | RODENHUIZE | 380 / T 1 | 380 | 150 | 36 | 450 | 450 | 15 | 17.99 | 2.18 | 1.24 | 1 | 12 | 24 | 1.5119 | 0.91583
ROMSE220T 8 220/ 70/15 T3 | ROMSE | ROMSEE | 220 / T 8 | 220 | 70 | 15 | 126.5 | 126.5 | 10 | 14.01 | 3.48 | 2.7 | 1 | 8 | 15 | -4.259 | -1.8929
SERAI220T 1 220/ 70/70 T3 | SERAI | SERAING | 220 / T 1 | 220 | 70 | 70 | 160 | 80 | 80 | 12.46 | 12.45 | 20.75 | 1 | 11 | 21 | 3.814 | 1.6951
SERAI220T 2 220/ 70 T2 | SERAI | SERAING | 220 / T 2 | 220 | 70 |  | 90 |  |  | 15.2 |  |  | 1 | 10 | 17 | -3.0857 | -1.3714
TERGN380T11 380/150/36 T3 | TERGN | TERGNEE | 380 / T11 | 380 | 150 | 36 | 450 | 450 | 15 | 17.82 | 2.17 | 1.28 | 1 | 12 | 24 | 1.5225 | 0.92396
TERGN380T12 380/150 T2 | TERGN | TERGNEE | 380 / T12 | 380 | 150 |  | 180 |  |  | 6.2 |  |  | 1 | 3 | 5 | 3.9 | 2.5
TIBIS380T 1 380/150/36 T3 | TIBIS | TIHANGE BIS | 380 / T 1 | 380 | 150 | 36 | 555 | 555 | 15 | 22.97 | 2.1 | 1.34 | 1 | 12 | 24 | 1.5208 | 0.92401
VANYK380D 1 380/380 T2 | VANYK | VAN EYCK | 380 / D 1 | 380 | 380 |  | 1400 |  |  | 9.32 |  |  | 1 | 18 | 35 | 1,47°
VANYK380D 2 380/380 T2 | VANYK | VAN EYCK | 380 / D 2 | 380 | 380 |  | 1400 |  |  | 9.31 |  |  | 1 | 18 | 35 | 1,47°
VERBT380T 1 380/150/36 T3 | VERBR | VERBRANDE BRUG | 380 / T 1 | 380 | 150 | 36 | 450 | 450 | 15 | 18.13 | 2.14 | 1.24 | 1 | 12 | 24 | 1.5217 | 0.92345
VERBT380T 2 380/150/36 T3 | VERBR | VERBRANDE BRUG | 380 / T 2 | 380 | 150 | 36 | 555 | 555 | 15 | 22.97 | 2.09 | 1.33 | 1 | 12 | 24 | 1.5208 | 0.92401
VILLE220T 1 220/ 70/15 T3 | VILLE | VILLEROUX | 220 / T 1 | 220 | 70 | 15 | 85 | 85 | 20 | 11.74 | 10.12 | 6.79 | 1 | 12 | 25 | -2.3077 | -1.049
VILLE220T 4 220/ 70/15 T3 | VILLE | VILLEROUX | 220 / T 4 | 220 | 70 | 15 | 90 | 90 | 5 | 11.33 | 4.14 | 5.04 | 1 | 11 | 21 | -3.3 | -1.5
ZANDV380D 1 380/380 T2 | ZANDV | ZANDVLIET | 380 / D 1 | 380 | 380 |  | 1400 |  |  | 9.31 |  |  |  | 18 |  | 1,47°
ZANDV380T 1 380/150/36 T3 | ZANDV | ZANDVLIET | 380 / T 1 | 380 | 150 | 36 | 500.1 | 500.1 | 15 | 19.86 | 2.17 | 1.23 | 1 | 12 | 24 | 1.5119 | 0.91583
ZANDV380T 2 380/150/36 T3 | ZANDV | ZANDVLIET | 380 / T 2 | 380 | 150 | 36 | 555 | 555 | 15 | 22.3 | 2 | 1.14 | 1 | 12 | 24 | 1.5208 | 0.92401